## Cons- Arab Aqsay
Project Title : AHF Drought Response Faryab - 01
Name | Arab Aqsay
Specification:- |  |  |  | Date
Construction of solar operated borehole with 10000 litre capacity of overhead tank through water network Pipe schemes |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Well drilling
1 | Conducting geophysical test for identification of proper location and depth for the borehole and the method of drilling. The test should be done with two different methods as follows to confirm each other. 1- Electromagnetic method: In this method at least 10 points should be measured till depth of 200m, to get the 2D graph of structure of earth layers. The location for borehole should be selected based on the graph. 2- Vertical Electrical Sounding (VES): The selected point should be investigated with VES till depth of at least 200m to get the strata properties and identify the depth of the aquifer. The equipment should be calibrated and able to record the data for all measured points in one file. The report, along with the raw data file, should be shared with SCI(in case the test failed at one point, the other Suitable points should be selected, and the new Geophysical test will be conducted in a new location, and the report should be shared with SCI). | it is contractor's responsibility to identify the right location using engineering instruments for bore well drilling as per TOR. | Test | 1
2 | Digging with 14" percussion drill with casing, well improvement and cleaning of around the well. If required, compression or rotary drill should be used for drilling hard layers. | As per instruction of SCI engineer | m | 120
3 | Supply and installation of PVC casing pipe class D (10 Kg/m), diameter of (8") inch Best quality from High Standard or Kawsar Company or any equivallent company. | As per instruction of SCI engineer | m | 80
4 | Supply and installation of PVC Filter pipe class D (10 Kg/m) diameter of (8") inch Best quality from High Standard or Kawsar Company. Transportation to the site is included | As per instruction of SCI engineer | m | 40
5 | Gravel Packing (River washed gravel) with material supply and installation | As per instruction of SCI engineer | cu.m | 8
6 | Pump test for determining of water discharge of well | As per instruction of SCI engineer | hour | 8
7 | Well header (cap) with steel Cover and Apron Structure with all material supply and installation. | As per instruction of SCI engineer | LS | 1
8 | well cleaning by and Well Chlorination including all required activities. | As per instruction of SCI engineer | LS | 1
9 | Certified Quality test of Water (Chemical, Physical and Biological) | As per TOR | LS | 1
Subtotal | [5 empty] | 0
USD
Solar Power pump system with transmission line from well to water Reservoir
10 | Submersible Pump (Grundfos company or equivalent) with 2.2KW- power and 180 m head, transportation included. Refer to pump design files. Please note that the Final Power of the submersible pump will be selected based on the pump test result, which will be done after drilling of the water well. | all accessories required (company certified) | pcs | 1
11 | Invertor+controller(Grundfos Company or other equivalent) with 4 KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
12 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 10
13 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 30
14 | Metalic inverter protection Box with door lock, attached to the Solar Pannel fram, size (800x600) mm | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
15 | Electric Cable (4*6)mm 3- phase cable for power as per system requirment. Turkish or equivalent quality with all supply, transport and installation. | As per instruction of SCI engineer | m | 150
16 | Grounding and earthing made of cupper and 2.5 meters length and 16mm dia with exothermic connections with all related activity and materials for all system (PV, Invertor, solar etc.). | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
17 | Safety rope for holding of pump 14 mm High Quality with supply and installation | As per instruction of SCI engineer | m | 300
Subtotal | [5 empty] | 0
USD
Construction of 10m3 (10000 liters) RCC Water tank with system
19 | Site Preparation | As per techical drawings and instruction of SCI engineer | M2 | 15.5636
20 | Excavation for Water Trough. | As per techical drawings and instruction of SCI engineer | M3 | 24.3794
21 | Earthwork Backfilling . | As per techical drawings and instruction of SCI engineer | M3 | 8.3424
22 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per techical drawings and instruction of SCI engineer | M3 | 1.6138
23 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per techical drawings and instruction of SCI engineer | M3 | 8.1337
24 | Plaster work with cement-sand, M: 1:3 inside with pedlow powder | As per techical drawings and instruction of SCI engineer | M2 | 32.16
25 | Plaster work with cement-sand, M: 1:3 Outside. | As per techical drawings and instruction of SCI engineer | M2 | 34.652
26 | Painting Plastic Wheather Sheet 2 Coat, please note that logo of save the children to be painted on one side of water tank. | As per techical drawings and instruction of SCI engineer | M2 | 20.64
27 | Supply and installation of Isogam insulation on roof of reservoir, thickness (4 - 5)mm ,weight (4.3-5.3)kg/m. | As per techical drawings and instruction of SCI engineer | M2 | 8.7616
28 | Supply and installation of iron gate for reservoir manhole (iron sheet 2mm thickness) along with lock and all required activities and as per drawing. | As per techical drawings and instruction of SCI engineer | Pcs | 1
29 | Supply and installation of 1 1/2 inch Galvanised Iron Ladder for reservoir with all required activites according to drawings. | As per techical drawings and instruction of SCI engineer | Pcs | 1
30 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for Inlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
31 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for outlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
32 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm Wash out pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
33 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm overflow pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
34 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 1 1/2" Outside Dia (48.8-47.9)mm Airflow pipe, wall thickness 3.2 mm ,weight 3.56 kg/m including wire mesh, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 3
35 | Supply and installation of Flanged Gate valve (Best quality) PN16, Nominal Diameter = 2" For Outlet Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
36 | Supply and installation of Flanged Gate valve (Best quality) PN16 , Nominal Diameter = 2" For Wash Out Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
37 | Supply and installation of Flunge Galvanized Iron Elbow, Nominal Diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
38 | Supply and installation of Galvanized Iron Elbow, Nominal Diameter 1 1/2". | As per techical drawings and instruction of SCI engineer | Pcs | 4
39 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
40 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 6
41 | Supply and installation of End cup for the wash out pipe 2" . | As per techical drawings and instruction of SCI engineer | Pcs | 1
42 | Glasswhool and GI sheet guage 24 for covering GI pipe . | As per techical drawings and instruction of SCI engineer | M2 | 10
43 | Supply and installation of PVC Dumbell with Center Bulb water stopper Width 18-23cm, Thickness 10mm Min Tensil strenght 12Mpa Confirming to IS12200 Of 1987 for joint between floor slab and walls insulation . | As per techical drawings and instruction of SCI engineer | M | 14
Sub-Total Cost for Construction 10 m3 RCC Drinking Water Reservior
USD
BoQ for RCC Part of Stand for Solar Panels
44 | Solar panel fixed Steel stand 25 and 45 Deg, Large (panels support structure), Steel angle iron (50x50x4) mm and steel girder (100x45x8)mm as per drawings along with anti-rust and painting . | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
45 | Excavation in different ground types 3 to 4. | As per instruction of SCI engineer/drawing | M3 | 0.245
46 | Filling Earthwork & Compacting . | As per instruction of SCI engineer/drawing | M3 | 0.1
47 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per instruction of SCI engineer/drawing | M3 | 0.05
48 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.129
49 | Graveling in foundation of solar stand Pillar. | As per instruction of SCI engineer/drawing | M3 | 0.05
50 | Plaster work with cement-sand M: 1:3. | As per instruction of SCI engineer/drawing | M2 | 0.81
51 | Painting 100% , Plastic Wheather Sheet 2 Coat, | As per instruction of SCI engineer/drawing | M2 | 0.81
No of Stand for Solar Panels | [5 empty] | 6
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of well protection box
52 | Excavation of foundation in ground type 3 - 5according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.9
53 | Back filling with Gravel under the PCC. | As per instruction of SCI engineer/drawing | M3 | 0.5
54 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.6
55 | Kilned brick masonry with mortar 1:4 (cement - sand) . | As per instruction of SCI engineer/drawing | M3 | 0.4
56 | Plaster work with cement + sand, M 150according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 3.5
57 | Plastic painting two coat for outside well protection 100%according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 2
58 | Steal Cover for well head (Well header) Size (60*60)sqm,from 4mm thick steel sheet ,with angle iron fram according to technical specifications. | As per instruction of SCI engineer/drawing | PCs | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BOQ for Valve Box
59 | Site Preparation | As per instruction of SCI engineer/drawing | M3 | 2.24
60 | Excavation for in ground type4- 5 . | As per instruction of SCI engineer/drawing | M3 | 1.7472
61 | Earthwork Backfilling . | As per instruction of SCI engineer/drawing | M3 | 0.8112
62 | Graveling . | As per instruction of SCI engineer/drawing | M3 | 0.168
63 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.639
64 | Plaster work with cement-sand, M: 1:3 . | As per instruction of SCI engineer/drawing | M2 | 5.76
65 | Valve 2 inch or 3 inch with fittings | As per instruction of SCI engineer/drawing | PCs | 2
| No of Valve Box |  |  |  |  | 3
| Sub-Total Cost for Construction of well protection(USD) |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
66 | Excavation and backfilling with soft soil and excavated materials of pipe trench for Transmission and Distribution Pipe laying in any ground type acoording to drawings. | As per techical drawings and instruction of SCI engineer | M3 | 500
67 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications.from well to water tank | As per techical drawings and instruction of SCI engineer | m | 300
68 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. main distribution pipe. | As per techical drawings and instruction of SCI engineer | m | 150
69 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074/8075 or AWWA C906-99.according to Technical Specs. | As per techical drawings and instruction of SCI engineer | m | 850
70 | Suppy and installation of fittings as per requirments of water supply network | As per techical drawings and instruction of SCI engineer | Lumpsum | 1
71 | Supply and installation of Brass Gate valve (Best quality) PN16 , Nominal Diameter = 2 ". With all its fittings and necessary items | As per techical drawings and instruction of SCI engineer | m | 1
Subtotal | [5 empty] | 0
USD
Public Stand taps
72 | Excavation in ground different type | As per techical drawings and instruction of SCI engineer | M3 | 0.57
73 | Back filling by soil as per drawing | As per techical drawings and instruction of SCI engineer | M3 | 0.5
74 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.5
75 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
76 | RCC (M:250, 1:1:2) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
77 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 1.5
78 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 1
No of Public Stand Taps | [5 empty] | 8
Subtotal | [5 empty] | 0
USD
79 | Project Sign board | As per techical drawings and instruction of SCI engineer | NO | 1
Grand Total |  |  |  |  | USD | 0

## Cons- Tutaki Hazarsum
Project Title :- AHF Drought Response Faryab
Name | Tutaki Hazarsum
Specification:- |  |  |  | Date
Construction of solar operated borehole with 10000 litre capacity of overhead tank through water network Pipe schemes |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Well drilling
1 | Conducting geophysical test for identification of proper location and depth for the borehole and the method of drilling. The test should be done with two different methods as follows to confirm each other. 1- Electromagnetic method: In this method at least 10 points should be measured till depth of 200m, to get the 2D graph of structure of earth layers. The location for borehole should be selected based on the graph. 2- Vertical Electrical Sounding (VES): The selected point should be investigated with VES till depth of at least 200m to get the strata properties and identify the depth of the aquifer. The equipment should be calibrated and able to record the data for all measured points in one file. The report, along with the raw data file, should be shared with SCI(in case the test failed at one point, the other Suitable points should be selected, and the new Geophysical test will be conducted in a new location, and the report should be shared with SCI). | it is contractor's responsibility to identify the right location using engineering instruments for bore well drilling as per TOR. | test | 1
2 | Digging with 14" percussion drill with casing, well improvement and cleaning of around the well. If required, compression or rotary drill should be used for drilling hard layers. | As per instruction of SCI engineer | m | 140
3 | Supply and installation of PVC casing pipe class D (10 Kg/m), diameter of (8") inch Best quality from High Standard or Kawsar Company or any equivallent company. | As per instruction of SCI engineer | m | 90
4 | Supply and installation of PVC Filter pipe class D (10 Kg/m) diameter of (8") inch Best quality from High Standard or Kawsar Company. Transportation to the site is included | As per instruction of SCI engineer | m | 50
5 | Gravel Packing (River washed gravel) with material supply and installation | As per instruction of SCI engineer | cu.m | 9
6 | Pump test for determining of water discharge of well | As per instruction of SCI engineer | hour | 8
7 | Well header (cap) with steel Cover and Apron Structure with all material supply and installation. | As per instruction of SCI engineer | LS | 1
8 | well cleaning by and Well Chlorination including all required activities. | As per instruction of SCI engineer | LS | 1
9 | Certified Quality test of Water (Chemical, Physical and Biological) | As per TOR | LS | 1
Subtotal | [5 empty] | 0
USD
Solar Power pump system with transmission line from well to water Reservoir
10 | Submersible Pump (Grundfos company or equivalent) with 2.2KW- power and 180 m head, transportation included. Refer to pump design files. Please note that the Final Power of the submersible pump will be selected based on the pump test result, which will be done after drilling of the water well. | all accessories required (company certified) | pcs | 1
11 | Invertor+controller(Grundfos Company or other equivalent) with 5 KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
12 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 12
13 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 30
14 | Metalic inverter protection Box with door lock, attached to the Solar Pannel fram, size (800x600) mm | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
15 | Electric Cable (4*6)mm 3- phase cable for power as per system requirment. Turkish or equivalent quality with all supply, transport and installation. | As per instruction of SCI engineer | m | 30
16 | Grounding and earthing made of cupper and 2.5 meters length and 16mm dia with exothermic connections with all related activity and materials for all system (PV, Invertor, solar etc.). | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
17 | Safety rope for holding of pump 14 mm High Quality with supply and installation | As per instruction of SCI engineer | m | 280
Subtotal | [5 empty] | 0
USD
Construction of 10m3 (10000 liters) RCC Water tank with system
18 | Site Preparation | As per techical drawings and instruction of SCI engineer | M2 | 15.5636
19 | Excavation for Water Trough. | As per techical drawings and instruction of SCI engineer | M3 | 24.3794
20 | Earthwork Backfilling . | As per techical drawings and instruction of SCI engineer | M3 | 8.3424
21 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per techical drawings and instruction of SCI engineer | M3 | 1.6138
22 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per techical drawings and instruction of SCI engineer | M3 | 8.1337
23 | Plaster work with cement-sand, M: 1:3 inside with pedlow powder | As per techical drawings and instruction of SCI engineer | M2 | 32.16
24 | Plaster work with cement-sand, M: 1:3 Outside. | As per techical drawings and instruction of SCI engineer | M2 | 34.652
25 | Painting 100% , Plastic Wheather Sheet 2 Coat, please note that logo of save the children to be painted on one side of water tank. | As per techical drawings and instruction of SCI engineer | M2 | 20.64
26 | Supply and installation of Isogam insulation on roof of reservoir, thickness (4 - 5)mm ,weight (4.3-5.3)kg/m. | As per techical drawings and instruction of SCI engineer | M2 | 8.7616
27 | Supply and installation of iron gate for reservoir manhole (iron sheet 2mm thickness) along with lock and all required activities and as per drawing. | As per techical drawings and instruction of SCI engineer | Pcs | 1
28 | Supply and installation of 1 1/2 inch Galvanised Iron Ladder for reservoir with all required activites according to drawings. | As per techical drawings and instruction of SCI engineer | Pcs | 1
29 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for Inlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
30 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for outlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
31 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm Wash out pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
32 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm overflow pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
33 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 1 1/2" Outside Dia (48.8-47.9)mm Airflow pipe, wall thickness 3.2 mm ,weight 3.56 kg/m including wire mesh, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 3
34 | Supply and installation of Flanged Gate valve (Best quality) PN16, Nominal Diameter = 2" For Outlet Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
35 | Supply and installation of Flanged Gate valve (Best quality) PN16 , Nominal Diameter = 2" For Wash Out Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
36 | Supply and installation of Flunge Galvanized Iron Elbow, Nominal Diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
37 | Supply and installation of Galvanized Iron Elbow, Nominal Diameter 1 1/2". | As per techical drawings and instruction of SCI engineer | Pcs | 4
38 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
39 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 6
40 | Supply and installation of End cup for the wash out pipe 2" . | As per techical drawings and instruction of SCI engineer | Pcs | 1
41 | Glasswhool and GI sheet guage 24 for covering GI pipe . | As per techical drawings and instruction of SCI engineer | M2 | 10
42 | Supply and installation of PVC Dumbell with Center Bulb water stopper Width 18-23cm, Thickness 10mm Min Tensil strenght 12Mpa Confirming to IS12200 Of 1987 for joint between floor slab and walls insulation . | As per techical drawings and instruction of SCI engineer | M | 14
| Sub-Total Cost for Construction 10 m3 RCC Drinking Water Reservior |  |  |  |  | 0
USD
BoQ for RCC Part of Stand for Solar Panels
43 | Solar panel fixed Steel stand 25 and 45 Deg, Large (panels support structure), Steel angle iron (50x50x4) mm and steel girder (100x45x8)mm as per drawings along with anti-rust and painting . | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
44 | Excavation in different ground types 3 to 4. | As per instruction of SCI engineer/drawing | M3 | 0.245
45 | Filling Earthwork & Compacting . | As per instruction of SCI engineer/drawing | M3 | 0.1
46 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per instruction of SCI engineer/drawing | M3 | 0.05
47 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.129
48 | Graveling in foundation of solar stand Pillar. | As per instruction of SCI engineer/drawing | M3 | 0.05
49 | Plaster work with cement-sand M: 1:3. | As per instruction of SCI engineer/drawing | M2 | 0.81
50 | Painting Plastic Wheather Sheet 2 Coat . | As per instruction of SCI engineer/drawing | M2 | 0.81
No of Stand for Solar Panels | [5 empty] | 6
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of well protection box
51 | Excavation of foundation in ground type 3 - 5according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.9
52 | Back filling with Gravel under the PCC. | As per instruction of SCI engineer/drawing | M3 | 0.5
53 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.6
54 | Kilned brick masonry with mortar 1:4 (cement - sand) . | As per instruction of SCI engineer/drawing | M3 | 0.4
55 | Plaster work with cement + sand, M 150according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 3.5
56 | Plastic painting two coat for outside well protection 100%according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 2
57 | Steal Cover for well head (Well header) Size (60*60)sqm,from 4mm thick steel sheet ,with angle iron fram according to technical specifications. | As per instruction of SCI engineer/drawing | PCs | 1
| Sub-Total Cost for Construction of well protection(USD) |  |  |  |  | 0
USD
BOQ for Valve Box
58 | Site Preparation | As per instruction of SCI engineer/drawing | M3 | 2.24
59 | Excavation for in ground type4- 5 . | As per instruction of SCI engineer/drawing | M3 | 1.7472
60 | Earthwork Backfilling . | As per instruction of SCI engineer/drawing | M3 | 0.8112
61 | Graveling . | As per instruction of SCI engineer/drawing | M3 | 0.168
62 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.639
63 | Plaster work with cement-sand, M: 1:3 . | As per instruction of SCI engineer/drawing | M2 | 5.76
64 | Valve 2 inch or 3 inch with fittings | As per instruction of SCI engineer/drawing | PCs | 2
| No of Valve Box |  |  |  |  | 3
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
65 | Excavation and backfilling with soft soil and excavated materials of pipe trench for Transmission and Distribution Pipe laying in any ground type acoording to drawings. | As per techical drawings and instruction of SCI engineer | M3 | 500
66 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications.from well to water tank | As per techical drawings and instruction of SCI engineer | m | 180
67 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. main distribution pipe. | As per techical drawings and instruction of SCI engineer | m | 150
68 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074/8075 or AWWA C906-99.according to Technical Specs. | As per techical drawings and instruction of SCI engineer | m | 550
69 | Supply and installation of Brass Gate valve (Best quality) PN16 , Nominal Diameter = 2 ". With all its fittings and necessary items | As per techical drawings and instruction of SCI engineer | m | 1
70 | Suppy and installation of fittings as per requirments of water supply network | As per techical drawings and instruction of SCI engineer | Lumpsum | 1
Subtotal | [5 empty] | 0
USD
Public Stand taps
71 | Excavation in ground different type | As per techical drawings and instruction of SCI engineer | M3 | 0.57
72 | Back filling by soil as per drawing | As per techical drawings and instruction of SCI engineer | M3 | 0.5
73 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.5
74 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
75 | RCC (M:250, 1:1:2) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
76 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 1.5
77 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 1
No of Public Stand Taps | [5 empty] | 7
Subtotal | [5 empty] | 0
USD
78 | Project Sign board | As per techical drawings and instruction of SCI engineer | NO | 1
Grand Total |  |  |  |  | USD | 0

## Cons - Tokali Hazarsum
Project Title :- AHF Drought Response Faryab - 01
Name | Tokali Hazarsum
Specification:- |  |  |  | Date
Construction of solar operated borehole with 20,000 litre capacity of overhead tank through water network Pipe schemes |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Well drilling
1 | Conducting geophysical test for identification of proper location and depth for the borehole and the method of drilling. The test should be done with two different methods as follows to confirm each other. 1- Electromagnetic method: In this method at least 10 points should be measured till depth of 200m, to get the 2D graph of structure of earth layers. The location for borehole should be selected based on the graph. 2- Vertical Electrical Sounding (VES): The selected point should be investigated with VES till depth of at least 200m to get the strata properties and identify the depth of the aquifer. The equipment should be calibrated and able to record the data for all measured points in one file. The report, along with the raw data file, should be shared with SCI(in case the test failed at one point, the other Suitable points should be selected, and the new Geophysical test will be conducted in a new location, and the report should be shared with SCI). | it is contractor's responsibility to identify the right location using engineering instruments for bore well drilling as per TOR. | test | 1
2 | Digging with a 14" percussion drill with casing, well improvement and cleaning of around the well. If required, compression or rotary drill should be used for drilling hard layers. | As per instruction of SCI engineer | m | 140
3 | Supply and installation of PVC casing pipe class D (10 Kg/m), diameter of (8") inch Best quality from High Standard or Kawsar Company or any equivallent company. | As per instruction of SCI engineer | m | 90
4 | Supply and installation of PVC Filter pipe class D (10 Kg/m) diameter of (8") inch Best quality from High Standard or Kawsar Company. Transportation to the site is included | As per instruction of SCI engineer | m | 50
5 | Gravel Packing (River washed gravel) with material supply and installation | As per instruction of SCI engineer | cu.m | 2
6 | Pump test for determining of water discharge of well | As per instruction of SCI engineer | hour | 8
7 | Well header (cap) with steel Cover and Apron Structure with all material supply and installation. | As per instruction of SCI engineer | LS | 1
8 | well cleaning by and Well Chlorination including all required activities. | As per instruction of SCI engineer | LS | 1
9 | Certified Quality test of Water (Chemical, Physical and Biological) | As per TOR | LS | 1
Subtotal | [5 empty] | 0
USD
Solar Power pump system with transmission line from well to water Reservoir
10 | Submersible Pump (Grundfos company or equivalent) with 2.2KW- power and 200m head, transportation included. Refer to pump design files. Please note that the Final Power of the submersible pump will be selected based on the pump test result, which will be done after drilling of the water well. | all accessories required (company certified) | pcs | 1
11 | Invertor+controller(Grundfos Company or other equivalent) with 5KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
12 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 12
13 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 50
14 | Metalic inverter protection Box with door lock, attached to the Solar Pannel fram, size (800x600) mm | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
15 | Electric Cable (4*6)mm 3- phase cable for power as per system requirment. Turkish or equivalent quality with all supply, transport and installation. | As per instruction of SCI engineer | m | 300
16 | Grounding and earthing made of cupper and 2.5 meters length and 16mm dia with exothermic connections with all related activity and materials for all system (PV, Invertor, solar etc.). | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
17 | Suppy and installation of fittings as per requirments of water supply network | As per techical drawings and instruction of SCI engineer | Lumpsum | 1
18 | Safety rope for holding of pump 14 mm High Quality with supply and installation | As per instruction of SCI engineer | m | 290
Subtotal | [5 empty] | 0
USD
Construction of 20m3 (20000 liters) RCC Water tank with system
19 | Excavation in any ground type. | As per attached Drawings and instruction of SCI Engineer | m3 | 28
20 | Soil back filling with compaction پرکاری خاک معه تپک کاری | As per attached Drawings and instruction of SCI Engineer | m3 | 15
21 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) کانکریت بدون سیخ با مارک مخلوطی (1:2:4) | As per attached Drawings and instruction of SCI Engineer | m3 | 2.3
22 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings 1:1.5:3 کانکریت سیخدار با مارک مخلوطی 1:1.5:3 همرای قالب بندی | As per attached Drawings and instruction of SCI Engineer | m3 | 12.2
23 | Plaster work with cement-sand + pad low powder in side the water tank M: 1:3 پلسترکاری با مخلوط سمنت وریگ وپودرضد نفوذ آب مارک مخلوط مصاله 1:3 | As per attached Drawings and instruction of SCI Engineer | m2 | 36
24 | Plaster work with cement-sand out side the water tank M: 1:3 پلسترکاری خارجی با مخلوط سمنت وریگ مارک مخلوط مصاله 1:3 | As per attached Drawings and instruction of SCI Engineer | m2 | 50
25 | Isograms insulation of reservoir roof ایزوگام برای پوشش بام ذخیره | As per attached Drawings and instruction of SCI Engineer | m2 | 15
26 | Supply and installation of iron gate for reservoir manhole (iron 20 gauge) with all required activities and as per drawing. تهیه ونصب دروازه فلزی از آهن چادر 20 گیچ همراه با ملحقات آن مطابقه نقشه | As per attached Drawings and instruction of SCI Engineer | No | 1
27 | Supply and installation of Galvanized Iron Ladder for reservoir with all required activates according to drawings. تهیه ونصب زینه مطابق نقشه همراه با تمام ملحقات آن مطابق نقشه | As per attached Drawings and instruction of SCI Engineer | No | 1
28 | pipes and fitting for water tank as per attached drawing | As per attached Drawings and instruction of SCI Engineer | LS | 1
29 | Painting 100% , Plastic Wheather Sheet 2 Coat, please note that logo of save the children to be painted on one side of water tank. | As per attached Drawings and instruction of SCI Engineer | M2 | 20.64
| Sub-Total Cost for Construction 20 m3 RCC Drinking Water Reservior |  |  |  |  | 0
USD
BoQ for RCC Part of Stand for Solar Panels
30 | Solar panel fixed Steel stand 25 and 45 Deg, Large (panels support structure), Steel angle iron (50x50x4) mm and steel girder (100x45x8)mm as per drawings along with anti-rust and painting . | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
31 | Excavation in different ground types 3 to 4. | As per instruction of SCI engineer/drawing | M3 | 0.245
32 | Filling Earthwork & Compacting . | As per instruction of SCI engineer/drawing | M3 | 0.1
33 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per instruction of SCI engineer/drawing | M3 | 0.05
34 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.129
35 | Graveling in foundation of solar stand Pillar. | As per instruction of SCI engineer/drawing | M3 | 0.05
36 | Plaster work with cement-sand M: 1:3. | As per instruction of SCI engineer/drawing | M2 | 0.81
37 | Painting Plastic Wheather Sheet 2 Coat . | As per instruction of SCI engineer/drawing | M2 | 0.81
No of Stand for Solar Panels | [5 empty] | 6
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of well protection box
38 | Excavation of foundation in ground type 3 - 5according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.9
39 | Back filling with Gravel under the PCC. | As per instruction of SCI engineer/drawing | M3 | 0.5
40 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.6
41 | Kilned brick masonry with mortar 1:4 (cement - sand) . | As per instruction of SCI engineer/drawing | M3 | 0.4
42 | Plaster work with cement + sand, M 150according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 3.5
43 | Plastic painting two coat for outside well protection 100%according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 2
44 | Steal Cover for well head (Well header) Size (60*60)sqm,from 4mm thick steel sheet ,with angle iron fram according to technical specifications. | As per instruction of SCI engineer/drawing | PCs | 1
| Sub-Total Cost for Construction of well protection(USD) |  |  |  |  | 0
USD
BOQ for Valve Box
45 | Site Preparation | As per instruction of SCI engineer/drawing | M3 | 2.24
46 | Excavation for in ground type4- 5 . | As per instruction of SCI engineer/drawing | M3 | 1.7472
47 | Earthwork Backfilling . | As per instruction of SCI engineer/drawing | M3 | 0.8112
48 | Graveling . | As per instruction of SCI engineer/drawing | M3 | 0.168
49 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.639
50 | Plaster work with cement-sand, M: 1:3 . | As per instruction of SCI engineer/drawing | M2 | 5.76
51 | Valve 2 inch or 3 inch with fittings | As per instruction of SCI engineer/drawing | PCs | 2
| No of Valve Box |  |  |  |  | 4
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
52 | Excavation and backfilling with soft soil and excavated materials of pipe trench for Transmission and Distribution Pipe laying in any ground type acoording to drawings. | As per techical drawings and instruction of SCI engineer | M3 | 1350
53 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications.from well to water tank | As per techical drawings and instruction of SCI engineer | m | 550
54 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. main distribution pipe. | As per techical drawings and instruction of SCI engineer | m | 200
55 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074/8075 or AWWA C906-99.according to Technical Specs. | As per techical drawings and instruction of SCI engineer | m | 2300
56 | Supply and installation of Brass Gate valve (Best quality) PN16 , Nominal Diameter = 2 ". With all its fittings and necessary items | As per techical drawings and instruction of SCI engineer | m | 1
57 | Suppy and installation of fittings as per requirments of water supply network | As per techical drawings and instruction of SCI engineer | Lumpsum | 1
Subtotal | [5 empty] | 0
USD
Public Stand taps
58 | Excavation in ground different type | As per techical drawings and instruction of SCI engineer | M3 | 0.57
59 | Back filling by soil as per drawing | As per techical drawings and instruction of SCI engineer | M3 | 0.5
60 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.5
61 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
62 | RCC (M:250, 1:1:2) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
63 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 1.5
64 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 1
No of Public Stand Taps | [5 empty] | 15
Subtotal | [5 empty] | 0
USD
65 | Project Sign board | As per techical drawings and instruction of SCI engineer | NO | 1
Grand Total |  |  |  |  | USD | 0

## Cons - Kolanie
Project Title :- AHF Drought Response Faryab - 01
Name | Kolanie
Specification:- |  |  |  | Date
Construction of solar operated borehole with 10000 litre capacity of overhead tank through water network Pipe schemes |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Well drilling
1 | Conducting geophysical test for identification of proper location and depth for the borehole and the method of drilling. The test should be done with two different methods as follows to confirm each other. 1- Electromagnetic method: In this method at least 10 points should be measured till depth of 200m, to get the 2D graph of structure of earth layers. The location for borehole should be selected based on the graph. 2- Vertical Electrical Sounding (VES): The selected point should be investigated with VES till depth of at least 200m to get the strata properties and identify the depth of the aquifer. The equipment should be calibrated and able to record the data for all measured points in one file. The report, along with the raw data file, should be shared with SCI(in case the test failed at one point, the other Suitable points should be selected, and the new Geophysical test will be conducted in a new location, and the report should be shared with SCI). | it is contractor's responsibility to identify the right location using engineering instruments for bore well drilling as per TOR. | test | 1
2 | Digging with 14" percussion drill with casing, well improvement and cleaning of around the well. If required, compression or rotary drill should be used for drilling hard layers. | As per instruction of SCI engineer | m | 120
3 | Supply and installation of PVC casing pipe class D (10 Kg/m), diameter of (8") inch Best quality from High Standard or Kawsar Company or any equivallent company. | As per instruction of SCI engineer | m | 80
4 | Supply and installation of PVC Filter pipe class D (10 Kg/m) diameter of (8") inch Best quality from High Standard or Kawsar Company. Transportation to the site is included | As per instruction of SCI engineer | m | 40
5 | Gravel Packing (River washed gravel) with material supply and installation | As per instruction of SCI engineer | cu.m | 2
6 | Pump test for determining of water discharge of well | As per instruction of SCI engineer | hour | 8
7 | Well header (cap) with steel Cover and Apron Structure with all material supply and installation. | As per instruction of SCI engineer | LS | 1
8 | well cleaning by and Well Chlorination including all required activities. | As per instruction of SCI engineer | LS | 1
9 | Certified Quality test of Water (Chemical, Physical and Biological) | As per TOR | LS | 1
Subtotal | [5 empty] | 0
USD
Solar Power pump system with transmission line from well to water Reservoir
10 | Submersible Pump (Grundfos company or equivalent) with 2.2KW- power and 180 m head, transportation included. Refer to pump design files. Please note that the Final Power of the submersible pump will be selected based on the pump test result, which will be done after drilling of the water well. | all accessories required (company certified) | pcs | 1
11 | Invertor+controller(Grundfos Company or other equivalent) with 4 KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
12 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 10
13 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 30
14 | Metalic inverter protection Box with door lock, attached to the Solar Pannel fram, size (800x600) mm | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
15 | Electric Cable (4*6)mm 3- phase cable for power as per system requirment. Turkish or equivalent quality with all supply, transport and installation. | As per instruction of SCI engineer | m | 150
16 | Grounding and earthing made of cupper and 2.5 meters length and 16mm dia with exothermic connections with all related activity and materials for all system (PV, Invertor, solar etc.). | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
17 | Suppy and installation of fittings as per requirments of water supply network | As per techical drawings and instruction of SCI engineer | Lumpsum | 1
18 | Safety rope for holding of pump 14 mm High Quality with supply and installation | As per instruction of SCI engineer | m | 300
Subtotal | [5 empty] | 0
USD
Construction of 10m3 (10000 liters) RCC Water tank with system
19 | Site Preparation | As per techical drawings and instruction of SCI engineer | M2 | 15.5636
20 | Excavation for Water Trough. | As per techical drawings and instruction of SCI engineer | M3 | 24.3794
21 | Earthwork Backfilling . | As per techical drawings and instruction of SCI engineer | M3 | 8.3424
22 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per techical drawings and instruction of SCI engineer | M3 | 1.6138
23 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per techical drawings and instruction of SCI engineer | M3 | 8.1337
24 | Plaster work with cement-sand, M: 1:3 inside with pedlow powder | As per techical drawings and instruction of SCI engineer | M2 | 32.16
25 | Plaster work with cement-sand, M: 1:3 Outside. | As per techical drawings and instruction of SCI engineer | M2 | 34.652
26 | Painting 100% , Plastic Wheather Sheet 2 Coat, please note that logo of save the children to be painted on one side of water tank. | As per techical drawings and instruction of SCI engineer | M2 | 20.64
27 | Supply and installation of Isogam insulation on roof of reservoir, thickness (4 - 5)mm ,weight (4.3-5.3)kg/m. | As per techical drawings and instruction of SCI engineer | M2 | 8.7616
28 | Supply and installation of iron gate for reservoir manhole (iron sheet 2mm thickness) along with lock and all required activities and as per drawing. | As per techical drawings and instruction of SCI engineer | Pcs | 1
29 | Supply and installation of 1 1/2 inch Galvanised Iron Ladder for reservoir with all required activites according to drawings. | As per techical drawings and instruction of SCI engineer | Pcs | 1
30 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for Inlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
31 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for outlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
32 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm Wash out pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
33 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm overflow pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
34 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 1 1/2" Outside Dia (48.8-47.9)mm Airflow pipe, wall thickness 3.2 mm ,weight 3.56 kg/m including wire mesh, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 3
35 | Supply and installation of Flanged Gate valve (Best quality) PN16, Nominal Diameter = 2" For Outlet Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
36 | Supply and installation of Flanged Gate valve (Best quality) PN16 , Nominal Diameter = 2" For Wash Out Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
37 | Supply and installation of Flunge Galvanized Iron Elbow, Nominal Diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
38 | Supply and installation of Galvanized Iron Elbow, Nominal Diameter 1 1/2". | As per techical drawings and instruction of SCI engineer | Pcs | 4
39 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
40 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 6
41 | Supply and installation of End cup for the wash out pipe 2" . | As per techical drawings and instruction of SCI engineer | Pcs | 1
42 | Glasswhool and GI sheet guage 24 for covering GI pipe . | As per techical drawings and instruction of SCI engineer | M2 | 10
43 | Supply and installation of PVC Dumbell with Center Bulb water stopper Width 18-23cm, Thickness 10mm Min Tensil strenght 12Mpa Confirming to IS12200 Of 1987 for joint between floor slab and walls insulation . | As per techical drawings and instruction of SCI engineer | M | 14
| Sub-Total Cost for Construction 10 m3 RCC Drinking Water Reservior |  |  |  |  | 0
USD
BoQ for RCC Part of Stand for Solar Panels
44 | Solar panel fixed Steel stand 25 and 45 Deg, Large (panels support structure), Steel angle iron (50x50x4) mm and steel girder (100x45x8)mm as per drawings along with anti-rust and painting . | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
45 | Excavation in different ground types 3 to 4. | As per instruction of SCI engineer/drawing | M3 | 0.245
46 | Filling Earthwork & Compacting . | As per instruction of SCI engineer/drawing | M3 | 0.1
47 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per instruction of SCI engineer/drawing | M3 | 0.05
48 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.129
49 | Graveling in foundation of solar stand Pillar. | As per instruction of SCI engineer/drawing | M3 | 0.05
50 | Plaster work with cement-sand M: 1:3. | As per instruction of SCI engineer/drawing | M2 | 0.81
51 | Painting Plastic Wheather Sheet 2 Coat . | As per instruction of SCI engineer/drawing | M2 | 0.81
No of Stand for Solar Panels | [5 empty] | 6
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
Steel Mesh Net and Fence Wall
52 | Fence Sourding for Solar Panel Dia Wire should not be less than 3mm along with 2 inch GI pipe (OD 60.2-59.3,thickness 2.6mm,Weight 3.66Kg/m Grade M As per BS 1387:1985) for the pole of the fence for the supporting on the top of the fence and for support between the two stands support for barbed wire along with GI circular barbed wire Circular Dia 50cm best quality according to given drawings with Installation (length= 10m and width= 10m). | the Mesh Net will be good quality, As per instruction of the SCI Engineer | LS | 1
Subtotal | [5 empty] | 0
USD
BoQ for Construction of well protection box
53 | Excavation of foundation in ground type 3 - 5according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.9
54 | Back filling with Gravel under the PCC. | As per instruction of SCI engineer/drawing | M3 | 0.5
55 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.6
56 | Kilned brick masonry with mortar 1:4 (cement - sand) . | As per instruction of SCI engineer/drawing | M3 | 0.4
57 | Plaster work with cement + sand, M 150according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 3.5
58 | Plastic painting two coat for outside well protection 100%according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 2
59 | Steal Cover for well head (Well header) Size (60*60)sqm,from 4mm thick steel sheet ,with angle iron fram according to technical specifications. | As per instruction of SCI engineer/drawing | PCs | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BOQ for Valve Box
60 | Site Preparation | As per instruction of SCI engineer/drawing | M3 | 2.24
61 | Excavation for in ground type4- 5 . | As per instruction of SCI engineer/drawing | M3 | 1.7472
62 | Earthwork Backfilling . | As per instruction of SCI engineer/drawing | M3 | 0.8112
63 | Graveling . | As per instruction of SCI engineer/drawing | M3 | 0.168
64 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.639
65 | Plaster work with cement-sand, M: 1:3 . | As per instruction of SCI engineer/drawing | M2 | 5.76
66 | Valve 2 inch or 3 inch with fittings | As per instruction of SCI engineer/drawing | PCs | 2
| No of Valve Box |  |  |  |  | 3
| Sub-Total Cost for Construction of well protection(USD) |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
67 | Excavation and backfilling with soft soil and excavated materials of pipe trench for Transmission and Distribution Pipe laying in any ground type acoording to drawings. | As per techical drawings and instruction of SCI engineer | M3 | 475
68 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications.from well to water tank | As per techical drawings and instruction of SCI engineer | m | 60
69 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. main distribution pipe. | As per techical drawings and instruction of SCI engineer | m | 60
70 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074/8075 or AWWA C906-99.according to Technical Specs. | As per techical drawings and instruction of SCI engineer | m | 950
71 | Supply and installation of Brass Gate valve (Best quality) PN16 , Nominal Diameter = 2 ". With all its fittings and necessary items | As per techical drawings and instruction of SCI engineer | m | 1
Subtotal | [5 empty] | 0
USD
Public Stand taps
72 | Excavation in ground different type | As per techical drawings and instruction of SCI engineer | M3 | 0.57
73 | Back filling by soil as per drawing | As per techical drawings and instruction of SCI engineer | M3 | 0.5
74 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.5
75 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
76 | RCC (M:250, 1:1:2) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
77 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 1.5
78 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 1
No of Public Stand Taps | [5 empty] | 8
Subtotal | [5 empty] | 0
USD
pipe transition between two hills
79 | Stone masonry with 35% mortar( M:300,1 :4 ) | As per instruction of SCI engineer | m3 | 8
80 | supply and installation of I beam 14 cm inside of stone mansonry for holding steel cable | As per instruction of SCI engineer | m | 4
81 | supply and installation of GI 3 inch pipe with fittings required. | As per instruction of SCI engineer | m | 100
82 | supply and installation of Steel cable 12mm for holding water pipe including needed U clamps | As per instruction of SCI engineer | m | 100
1
| subtotal of pipe transition between two hills |  |  |  |  | 0
USD
83 | Project Sign board | As per techical drawings and instruction of SCI engineer | NO | 1
Grand Total |  |  |  |  | USD | 0

## Cons - Pawgani Yamaq
Project Title :- AHF Drought Response Faryab - 01
Name | Pawgani Yamaq
Specification:- |  |  |  | Date
Construction of solar operated borehole with 10000 litre capacity of overhead tank through water network Pipe schemes |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Well drilling
1 | Conducting geophysical test for identification of proper location and depth for the borehole and the method of drilling. The test should be done with two different methods as follows to confirm each other. 1- Electromagnetic method: In this method at least 10 points should be measured till depth of 200m, to get the 2D graph of structure of earth layers. The location for borehole should be selected based on the graph. 2- Vertical Electrical Sounding (VES): The selected point should be investigated with VES till depth of at least 200m to get the strata properties and identify the depth of the aquifer. The equipment should be calibrated and able to record the data for all measured points in one file. The report, along with the raw data file, should be shared with SCI(in case the test failed at one point, the other Suitable points should be selected, and the new Geophysical test will be conducted in a new location, and the report should be shared with SCI). | it is contractor's responsibility to identify the right location using engineering instruments for bore well drilling as per TOR. | test | 1
2 | Digging with 14" percussion drill with casing, well improvement and cleaning of around the well. If required, compression or rotary drill should be used for drilling hard layers. | As per instruction of SCI engineer | m | 140
3 | Supply and installation of PVC casing pipe class D (10 Kg/m), diameter of (8") inch Best quality from High Standard or Kawsar Company or any equivallent company. | As per instruction of SCI engineer | m | 90
4 | Supply and installation of PVC Filter pipe class D (10 Kg/m) diameter of (8") inch Best quality from High Standard or Kawsar Company. Transportation to the site is included | As per instruction of SCI engineer | m | 50
5 | Gravel Packing (River washed gravel) with material supply and installation | As per instruction of SCI engineer | cu.m | 2
6 | Pump test for determining of water discharge of well | As per instruction of SCI engineer | hour | 8
7 | Well header (cap) with steel Cover and Apron Structure with all material supply and installation. | As per instruction of SCI engineer | LS | 1
8 | well cleaning by and Well Chlorination including all required activities. | As per instruction of SCI engineer | LS | 1
9 | Certified Quality test of Water (Chemical, Physical and Biological) | As per TOR | LS | 1
Subtotal | [5 empty] | 0
USD
Solar Power pump system with transmission line from well to water Reservoir
10 | Submersible Pump (Grundfos company or equivalent) with 2.2KW- power and 200 m head, transportation included. Refer to pump design files. Please note that the Final Power of the submersible pump will be selected based on the pump test result, which will be done after drilling of the water well. | all accessories required (company certified) | pcs | 1
11 | Invertor+controller(Grundfos Company or other equivalent) with 4 KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
12 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 10
13 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 50
14 | Metalic inverter protection Box with door lock, attached to the Solar Pannel fram, size (800x600) mm | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
15 | Electric Cable (4*6)mm 3- phase cable for power as per system requirment. Turkish or equivalent quality with all supply, transport and installation. | As per instruction of SCI engineer | m | 200
16 | Grounding and earthing made of cupper and 2.5 meters length and 16mm dia with exothermic connections with all related activity and materials for all system (PV, Invertor, solar etc.). | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
17 | Suppy and installation of fittings as per requirments of water supply network | As per techical drawings and instruction of SCI engineer | Lumpsum | 1
18 | Safety rope for holding of pump 14 mm High Quality with supply and installation | As per instruction of SCI engineer | m | 290
Subtotal | [5 empty] | 0
USD
Construction of 10m3 (10000 liters) RCC Water tank with system
19 | Site Preparation | As per techical drawings and instruction of SCI engineer | M2 | 15.5636
20 | Excavation for Water Trough. | As per techical drawings and instruction of SCI engineer | M3 | 24.3794
21 | Earthwork Backfilling . | As per techical drawings and instruction of SCI engineer | M3 | 8.3424
22 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per techical drawings and instruction of SCI engineer | M3 | 1.6138
23 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per techical drawings and instruction of SCI engineer | M3 | 8.1337
24 | Plaster work with cement-sand, M: 1:3 inside with pedlow powder | As per techical drawings and instruction of SCI engineer | M2 | 32.16
25 | Plaster work with cement-sand, M: 1:3 Outside. | As per techical drawings and instruction of SCI engineer | M2 | 34.652
26 | Painting 100% , Plastic Wheather Sheet 2 Coat, please note that logo of save the children to be painted on one side of water tank. | As per techical drawings and instruction of SCI engineer | M2 | 20.64
27 | Supply and installation of Isogam insulation on roof of reservoir, thickness (4 - 5)mm ,weight (4.3-5.3)kg/m. | As per techical drawings and instruction of SCI engineer | M2 | 8.7616
28 | Supply and installation of iron gate for reservoir manhole (iron sheet 2mm thickness) along with lock and all required activities and as per drawing. | As per techical drawings and instruction of SCI engineer | Pcs | 1
29 | Supply and installation of 1 1/2 inch Galvanised Iron Ladder for reservoir with all required activites according to drawings. | As per techical drawings and instruction of SCI engineer | Pcs | 1
30 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for Inlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
31 | Supply and Installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2 1/2" Outside Dia (76.6-75.3)mm for outlet pipe, wall thickness 3.6 mm ,weight 6.42 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
32 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm Wash out pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 4
33 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 2" Outside Dia (60.8-59.7)mm overflow pipe, wall thickness 3.6 mm ,weight 5.03 kg/m, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 6
34 | Supply and installaiton of Galvanized Iron (GI) pipe, Nominal Diameter 1 1/2" Outside Dia (48.8-47.9)mm Airflow pipe, wall thickness 3.2 mm ,weight 3.56 kg/m including wire mesh, Grade (M) as per BS1387:1985. | As per techical drawings and instruction of SCI engineer | M | 3
35 | Supply and installation of Flanged Gate valve (Best quality) PN16, Nominal Diameter = 2" For Outlet Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
36 | Supply and installation of Flanged Gate valve (Best quality) PN16 , Nominal Diameter = 2" For Wash Out Pipe. | As per techical drawings and instruction of SCI engineer | Pcs | 1
37 | Supply and installation of Flunge Galvanized Iron Elbow, Nominal Diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
38 | Supply and installation of Galvanized Iron Elbow, Nominal Diameter 1 1/2". | As per techical drawings and instruction of SCI engineer | Pcs | 4
39 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 10
40 | Supply and installation of Galvanized Flange Adapter, diameter 2". | As per techical drawings and instruction of SCI engineer | Pcs | 6
41 | Supply and installation of End cup for the wash out pipe 2" . | As per techical drawings and instruction of SCI engineer | Pcs | 1
42 | Glasswhool and GI sheet guage 24 for covering GI pipe . | As per techical drawings and instruction of SCI engineer | M2 | 10
43 | Supply and installation of PVC Dumbell with Center Bulb water stopper Width 18-23cm, Thickness 10mm Min Tensil strenght 12Mpa Confirming to IS12200 Of 1987 for joint between floor slab and walls insulation . | As per techical drawings and instruction of SCI engineer | M | 14
| Sub-Total Cost for Construction 10 m3 RCC Drinking Water Reservior |  |  |  |  | 0
USD
Steel Mesh Net and Fence Wall
44 | Fence Sourding for Solar Panel Dia Wire should not be less than 3mm along with 2 inch GI pipe (OD 60.2-59.3,thickness 2.6mm,Weight 3.66Kg/m Grade M As per BS 1387:1985) for the pole of the fence for the supporting on the top of the fence and for support between the two stands support for barbed wire along with GI circular barbed wire Circular Dia 50cm best quality according to given drawings with Installation (length= 10m and width= 10m). | the Mesh Net will be good quality, As per instruction of the SCI Engineer | LS | 1
Subtotal | [5 empty] | 0
USD
BoQ for RCC Part of Stand for Solar Panels
45 | Solar panel fixed Steel stand 25 and 45 Deg, Large (panels support structure), Steel angle iron (50x50x4) mm and steel girder (100x45x8)mm as per drawings along with anti-rust and painting . | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
46 | Excavation in different ground types 3 to 4. | As per instruction of SCI engineer/drawing | M3 | 0.245
47 | Filling Earthwork & Compacting . | As per instruction of SCI engineer/drawing | M3 | 0.1
48 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per instruction of SCI engineer/drawing | M3 | 0.05
49 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.129
50 | Graveling in foundation of solar stand Pillar. | As per instruction of SCI engineer/drawing | M3 | 0.05
51 | Plaster work with cement-sand M: 1:3. | As per instruction of SCI engineer/drawing | M2 | 0.81
52 | Painting Plastic Wheather Sheet 2 Coat . | As per instruction of SCI engineer/drawing | M2 | 0.81
No of Stand for Solar Panels | [5 empty] | 6
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of well protection box
53 | Excavation of foundation in ground type 3 - 5according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.9
54 | Back filling with Gravel under the PCC. | As per instruction of SCI engineer/drawing | M3 | 0.5
55 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.6
56 | Kilned brick masonry with mortar 1:4 (cement - sand) . | As per instruction of SCI engineer/drawing | M3 | 0.4
57 | Plaster work with cement + sand, M 150according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 3.5
58 | Plastic painting two coat for outside well protection 100%according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 2
59 | Steal Cover for well head (Well header) Size (60*60)sqm,from 4mm thick steel sheet ,with angle iron fram according to technical specifications. | As per instruction of SCI engineer/drawing | PCs | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BOQ for Valve Box
60 | Site Preparation | As per instruction of SCI engineer/drawing | M3 | 2.24
61 | Excavation for in ground type4- 5 . | As per instruction of SCI engineer/drawing | M3 | 1.7472
62 | Earthwork Backfilling . | As per instruction of SCI engineer/drawing | M3 | 0.8112
63 | Graveling . | As per instruction of SCI engineer/drawing | M3 | 0.168
64 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.639
65 | Plaster work with cement-sand, M: 1:3 . | As per instruction of SCI engineer/drawing | M2 | 5.76
66 | Valve 2 inch or 3 inch with fittings | As per instruction of SCI engineer/drawing | PCs | 2
| No of Valve Box |  |  |  |  | 4
| Sub-Total Cost for Construction of well protection(USD) |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
67 | Excavation and backfilling with soft soil and excavated materials of pipe trench for Transmission and Distribution Pipe laying in any ground type acoording to drawings. | As per techical drawings and instruction of SCI engineer | M3 | 520
68 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications.from well to water tank | As per techical drawings and instruction of SCI engineer | m | 430
69 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. main distribution pipe. | As per techical drawings and instruction of SCI engineer | m | 160
70 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074/8075 or AWWA C906-99.according to Technical Specs. | As per techical drawings and instruction of SCI engineer | m | 800
71 | Supply and installation of Brass Gate valve (Best quality) PN16 , Nominal Diameter = 2 ". With all its fittings and necessary items | As per techical drawings and instruction of SCI engineer | m | 1
Subtotal | [5 empty] | 0
USD
Public Stand taps
72 | Excavation in ground different type | As per techical drawings and instruction of SCI engineer | M3 | 0.57
73 | Back filling by soil as per drawing | As per techical drawings and instruction of SCI engineer | M3 | 0.5
74 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.5
75 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
76 | RCC (M:250, 1:1:2) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
77 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 1.5
78 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 1
No of Public Stand Taps | [5 empty] | 5
Subtotal | [5 empty] | 0
USD
79 | Project Sign board | As per techical drawings and instruction of SCI engineer | NO | 1
Grand Total |  |  |  |  | USD | 0