## Rehab - Kohna Qishlaq
Project Title :- AHF Drought Response Faryab
Name | Kohna Qishlaq
Specification:- |  |  |  | Date
Rehabilitation of water network |  |  |  | Provinces |  | Faryab | More information
Bill of Quantity (BoQ) | [6 empty] | GPS points | 35.76744° N, 64.70033° E
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD | well to Solar
water table
BoQ for Construction of well protection box
1 | Excavation of foundation in ground type 3 - 5according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.9
2 | Back filling with Gravel under the PCC. | As per instruction of SCI engineer/drawing | M3 | 0.5
3 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.6
4 | Kilned brick masonry with mortar 1:4 (cement - sand) . | As per instruction of SCI engineer/drawing | M3 | 0.4
5 | Plaster work with cement + sand, M 150according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 3.5
6 | Plastic painting two coat for outside well protection 100%according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 2
7 | Steel Cover for well head (Well header) Size (60*60)sqm,from 4mm thick steel sheet ,with angle iron fram according to technical specifications. | As per instruction of SCI engineer/drawing | PCs | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
8 | Excavation of pipe trench for Transmission and Distribution Pipe laying in any ground type and back filling | As per techical drawings and instruction of SCI engineer | M3 | 400
9 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074/8075 or AWWA C906-99.according to Technical Specs. | As per techical drawings and instruction of SCI engineer | m | 800
10 | Supply and installation of Brass Gate valve (Best quality) PN16 , Nominal Diameter = 2 ". With all its fittings and necessary items | As per techical drawings and instruction of SCI engineer | m | 1
Subtotal | [5 empty] | 0
USD
Public Stand taps
11 | Excavation in ground different type | As per techical drawings and instruction of SCI engineer | M3 | 0.57
12 | Back filling by soil as per drawing | As per techical drawings and instruction of SCI engineer | M3 | 0.5
13 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.5
14 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
15 | RCC (M:250, 1:1:2) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
16 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 1.5
17 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 1
No of Public Stand Taps | [5 empty] | 6
Subtotal | [5 empty] | 0
USD
Grand Total |  |  |  |  | USD | 0

## Rehab - Jamshidi Bala
Project Title :- AHF Drought Response Faryab
Name | Jamshidi bala
Specification:- |  |  |  | Date
Rehabilitation of water network |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Solar Power pump system with transmission line from well to water Reservoir
1 | Submersible Pump (Grundfos company or equivalent) with 3 KW- power and 200 m head, transportation included. Reffer to pumpe desing files,Please note that the Final Power of the submersible pump will be selected based on the pump test result of well. | all accessories required (company certified) | pcs | 1
2 | Invertor+controller(Grundfos Company or other equivalent) with 5KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
3 | AE Solar panels 270 watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):270W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 7
Subtotal | [5 empty] | 0
USD
rehabilitation of Public Stand taps
4 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.2
5 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.12
6 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 0.6
7 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 0.4
No of Public Stand Taps | [5 empty] | 42
Subtotal | [5 empty] | 0
USD
Grand Total |  |  |  |  | USD | 0

## Rehab -Jamshidi payeen
Project Title :- AHF Drought Response Faryab
Name | Jamshidi payeen
Specification:- |  |  |  | Date
Rehabilitation of water network |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Solar Power pump system with transmission line from well to water Reservoir
1 | Submersible Pump (Grundfos company or equivalent) with 2.2KW- power and 180 m head, transportation included. Reffer to pumpe desing files,Please note that the Final Power of the submersible pump will be selected based on the pump test result of well. | all accessories required (company certified) | pcs | 1
2 | Invertor+controller(Grundfos Company or other equivalent) with 4 KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
3 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 10
4 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 100
5 | Metalic inverter protection Box with door lock, attached to the Solar Pannel fram, size (800x600) mm | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
6 | Electric Cable (4*6)mm 3- phase cable for power as per system requirment. Turkish or equivalent quality with all supply, transport and installation. | As per instruction of SCI engineer | m | 150
7 | Grounding and earthing for all system (PV, Invertor, solar etc.) | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
8 | Safety rope for holding of pump 14 mm High Quality with supply and installation | As per instruction of SCI engineer | m | 140
Subtotal | [5 empty] | 0
USD
BoQ for RCC Part of Stand for Solar Panels
9 | Solar panel fixed Steel stand 25 and 45 Deg, Large (panels support structure), Steel angle iron (50x50x4) mm and steel girder (100x45x8)mm as per drawings along with anti-rust and painting . | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
10 | Excavation in different ground types 3 to 4. | As per instruction of SCI engineer/drawing | M3 | 0.245
11 | Filling Earthwork & Compacting . | As per instruction of SCI engineer/drawing | M3 | 0.1
12 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) along with Shuttring and Curing as per drawing . | As per instruction of SCI engineer/drawing | M3 | 0.05
13 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.129
14 | Graveling in foundation of solar stand Pillar. | As per instruction of SCI engineer/drawing | M3 | 0.05
15 | Plaster work with cement-sand M: 1:3. | As per instruction of SCI engineer/drawing | M2 | 0.81
16 | Painting Plastic Wheather Sheet 2 Coat . | As per instruction of SCI engineer/drawing | M2 | 0.81
No of Stand for Solar Panels | [5 empty] | 6
| Sub-Total Cost for Construction 10 m3 RCC Drinking Water Reservior |  |  |  |  | 6
USD
BoQ for Construction of well protection box
17 | Excavation of foundation in ground type 3 - 5according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.9
18 | Back filling with Gravel under the PCC. | As per instruction of SCI engineer/drawing | M3 | 0.5
19 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) according to Technical Specs. | As per instruction of SCI engineer/drawing | M3 | 0.6
20 | Kilned brick masonry with mortar 1:4 (cement - sand) . | As per instruction of SCI engineer/drawing | M3 | 0.4
21 | Plaster work with cement + sand, M 150according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 3.5
22 | Plastic painting two coat for outside well protection 100%according to Technical Specs. | As per instruction of SCI engineer/drawing | M2 | 2
23 | Steal Cover for well head (Well header) Size (60*60)sqm,from 4mm thick steel sheet ,with angle iron fram according to technical specifications. | As per instruction of SCI engineer/drawing | PCs | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
repairing of public Stand taps
24 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.2
25 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.12
26 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 0.6
27 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 0.4
No of Public Stand Taps | [5 empty] | 20
Subtotal | [5 empty] | 0
USD
Grand Total |  |  |  |  | USD

## Rehab - Imam sahib
Project Title :- AHF Drought Response Faryab
Name | Emam sahib
Specification:- |  |  |  | Date
Rehabilitation of water network |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Solar Power pump system with transmission line from well to water Reservoir
1 | Submersible Pump (Grundfos company or equivalent) with 2.2KW- power and 200 m head, transportation included. Reffer to pumpe desing files,Please note that the Final Power of the submersible pump will be selected based on the pump test result of well. | all accessories required (company certified) | pcs | 1
2 | Invertor+controller(Grundfos Company or other equivalent) with 4 KW Capacity High quality with supply and installation accessories required. | it is working both as controller and invertor | pcs | 1
3 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 12
4 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 50
5 | Metalic inverter protection Box with door lock, attached to the Solar Pannel fram, size (800x600) mm | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
6 | Electric Cable (4*6)mm 3- phase cable for power as per system requirment. Turkish or equivalent quality with all supply, transport and installation. | As per instruction of SCI engineer | m | 50
7 | Grounding and earthing for all system (PV, Invertor, solar etc.) | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
8 | Safety rope for holding of pump 14 mm High Quality with supply and installation | As per instruction of SCI engineer | m | 240
Subtotal | [5 empty] | 0
USD
BoQ for RCC Part of Stand for Solar Panels
9 | Solar panel fixed Steel stand 25 and 45 Deg, Large (panels support structure), Steel angle iron (50x50x4) mm and steel girder (100x45x8)mm as per drawings along with anti-rust and painting . | all accessories required as per given drawing & instruction of SCI Engineer | LS | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BOQ for Valve Box
10 | Site Preparation | As per instruction of SCI engineer/drawing | M3 | 2.24
11 | Excavation for in ground type4- 5 . | As per instruction of SCI engineer/drawing | M3 | 1.7472
12 | Earthwork Backfilling . | As per instruction of SCI engineer/drawing | M3 | 0.8112
13 | Graveling . | As per instruction of SCI engineer/drawing | M3 | 0.168
14 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | As per instruction of SCI engineer/drawing | M3 | 0.639
15 | Plaster work with cement-sand, M: 1:3 . | As per instruction of SCI engineer/drawing | M2 | 5.76
16 | Valve 2 inch or 3 inch with fittings | As per instruction of SCI engineer/drawing | PCs | 2
| No of Valve Box |  |  |  |  | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
17 | Excavation of pipe trench for Transmission and Distribution Pipe laying in any ground type and backfilling | As per techical drawings and instruction of SCI engineer | M3 | 290
18 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications.from well to water tank | As per techical drawings and instruction of SCI engineer | m | 30
19 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. main distribution pipe. | As per techical drawings and instruction of SCI engineer | m | 200
20 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074/8075 or AWWA C906-99.according to Technical Specs. | As per techical drawings and instruction of SCI engineer | m | 400
21 | Supply and installation of Brass Gate valve (Best quality) PN16 , Nominal Diameter = 2 ". With all its fittings and necessary items | As per techical drawings and instruction of SCI engineer | m | 1
Subtotal | [5 empty] | 0
USD
Public Stand taps - rehabilitation
22 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.2
23 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.12
24 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 0.6
25 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 0.4
No of Public Stand Taps | [5 empty] | 45
Subtotal | [5 empty] | 0
USD
Grand Total |  |  |  |  | USD | 0

## Rehab - Aq cheshma
Project Title :- AHF Drought Response Faryab
Name | Aq Cheshma
Specification:- |  |  |  | Date
Rehabilitation of water network |  |  |  | Provinces |  | Faryab
Bill of Quantity (BoQ)
items | Description of work/Items | Size/ Specification | Unit | Qty | Unit Cost USD | Total Cost USD
Solar Power pump system with transmission line from well to water Reservoir
1 | AE Solar panels 450watt internationally certified by IEC, ISO,TUV, and CE, Maximum Power(Wp):450W, MONOCRYSTALLINE, Water proof PV junction boxes IP68 for each array including DC switch disconnectors, bus bars, terminals, ducts or trays, supports & labels suitable to the PV arrays loads. | With all accessories required including all related items and electric cables. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 year. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company | pcs | 10
2 | electric cable (2*6)mm DC, from solar panel to inverter | As per instruction of SCI engineer | m | 50
Subtotal | [5 empty] | 0
USD
BoQ for Construction of spring protection structure as per attached drawing
3 | Site preparation | As per instruction of SCI engineer | m2 | 6
4 | Stone masonry with 35% mortar( M:300,1 :4 ) | As per instruction of SCI engineer | m3 | 6
5 | RCC ( M:250, 1:1:2 ) | As per instruction of SCI engineer | m3 | 1
6 | PCC (M:150, 1:2:4) | As per instruction of SCI engineer | m3 | 1
7 | Filling of Bolder stone in spring catchment | As per instruction of SCI engineer | m3 | 1
| Sub-Total Cost for Construction of well protection(AFN) |  |  |  |  | 0
USD
pipe transition between two hills
8 | Stone masonry with 35% mortar( M:300,1 :4 ) | As per instruction of SCI engineer | m3 | 4
9 | supply and installation of I beam 14 cm inside of stone mansonry for holding steel cable | As per instruction of SCI engineer | m | 4
10 | supply and installation of Steel cable 12mm for holding water pipe including needed U clamps | As per instruction of SCI engineer | m | 60
1
| subtotal of pipe transition between two hills |  |  |  |  | 0
USD
BoQ for Construction of transmission pipe , Tap Station and Soak away (Percolation) Pit
11 | Excavation of pipe trench for Transmission and Distribution Pipe laying in any ground type and backfilling | As per techical drawings and instruction of SCI engineer | M3 | 150
12 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications.from wspring to water tank | As per techical drawings and instruction of SCI engineer | m | 800
13 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. main distribution pipe. | As per techical drawings and instruction of SCI engineer | m | 160
Subtotal | [5 empty] | 0
USD
Public Stand taps - construction
14 | Excavation in ground different type | As per techical drawings and instruction of SCI engineer | M3 | 0.57
15 | Back filling by soil as per drawing | As per techical drawings and instruction of SCI engineer | M3 | 0.5
16 | Crush Gravel For stand tap | As per techical drawings and instruction of SCI engineer | M3 | 0.5
17 | PCC M150 kg/cm2 - (1:2:4) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
18 | RCC (M:250, 1:1:2) | As per techical drawings and instruction of SCI engineer | M3 | 0.3
19 | Plaster work with cement-sand M: 1:3 | As per techical drawings and instruction of SCI engineer | M2 | 1.5
20 | Fittings as per site need includding brass taps, saddle clamp, elbow, Tee connection … etc, complete work. | As per techical drawings and instruction of SCI engineer | Ls | 1
No of Public Stand Taps | [5 empty] | 5
Subtotal | [5 empty] | 0
USD
Grand Total |  |  |  |  | USD | 0