## BoreWell
Save the Children International
Provincial Office
Bill of Quantity -Solar system Borewell
برآورد چاه جدید به سیستم انرژی نورآفتاب
No | Description of work | مشخصات فعالیت | Unit | Quantity | Unit Cost (USD) | Total Cost (USD) | Remarks
1 | Connection from existing pipe shceme HDPE Pipe PN16 with installation (32mm Dia) with fittings and Installation | پیپ سیاه سخت (۱۶ بار) رسانده به ساحه ونصب آن | M | 150
2 | Water quality Test Biological and (PH, TDS, Turbidity, EC) by the standard laboratory, and Well Chlorination. | آزمایش کیفیت آب آزمایش بیولوژیکی و(PH, TDS, Turbidities) توسط آزمایش گاه معیاری وهم چنان کلوریشن آب چاه بعد ازحفاری. | Job | 1
3 | Equipment for water network as per attached drawing such as (water tap 1 inch, elbow 1-inch, Semitic 1inch, female elbow 1inch, three mouth PVC, phoom large&smal, elbow simple, water tap 3inch, three mouth 3inch…with all necessary) complete work for water point. As per site engineer guidance | اجزای ارتباط دهنده شبکه آبرسانی برای یک نقطه آبگیر باتمام امورات ایجابی آن شیردهن؛ زانو خم ؛ سه دهن ؛ پوم باتمام امورات ایجابی آن مکمل کار. | Set | 1
4 | Water reservoir with standing and installation, all necessary (according to- Drawing attached) and well protection Supply and installation of a 2,000-liter elevated cylindrical steel water reservoir fabricated from 3 mm thick steel plate, complete with three coats of protective paint inside and outside, 1-inch PVC overflow pipe, cleaning outlet with gate valve, and top access opening. The tank shall be mounted on a steel tower constructed of 4-inch diameter steel tubes (4 mm thick) with cross bracing and a 1-inch iron ladder for maintenance access. A circular steel walkway shall be provided around the tank. The structure shall include a lockable safety cage made of 2-inch GI pipe framing and 3 mm wire mesh and one door. The water distribution system shall include 1-inch diameter pipes with necessary valves and fittings. The tower shall be supported on an M-250 RCC foundation with PCC bedding, compacted gravel, and selected soil as per the approved drawing. | تهیه ونصب تانکرآب همراه بانصب آن وتمام امورات ایجابی آن مطابق به ( نقشه مهندسی ضمیمه شده است). | Set | 1
5 | Gate valve: PPR 1'' Gate valve with installation | تهیه ونصب ګیت وال یک انچ پی پی ار | PCs | 4
6 | Make and construct soak pit for water point From RCC R-100cm with 1.8m depth and adjust on work area (drawing attached). | تهیه وساخت soak pit از چک چاه بصورت آهن کانکریتی به شعاع ۵۰ سانتی متر اعمار مطابق به وضعیت ساحه مطابق به نقشه ضمیمه شده. | Set | 1
Total cost in USD | [5 empty] | 0
| Date : |  | Date :
| Signature : |  | Signature :